FC 280 Filter Cable Distances

FC 280 Filter Cable Distances

It was obtained using a system with frequency converter (with mounting  plate),  and protected motor cables.

| Filter type (internal) | Supply voltage/nominal power |  |  | Class A2/EN 55011 |  | Class A1/EN 55011 |  | Class B/EN 55011 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3x380-480 V | 3x200-240 V | 1x200-240 V | Executed | Spreading | Executed | Spreading | Executed | Spreading |
| A2 filter | 0.37-22 kW (0,5–30 hp) | – | – | 25 m (82 ft) | Yes1) | – | – | – | – |
|  | – | 0.37-4 kW (0,5–5,4 hp) | – | 25 m (82 ft) | Yes1) | – | – | – | – |
|  | – | – | 0.37-2.2 kW (0,5–3 hp) | – | – | – | – | – | – |
| A1 filter | 0.37-7.5 kW (0,5–10 hp) | – | – | 25 m (82 ft) | Yes1) | 25 m (£82) | Yes | – | – |
|  | 11-22 kW (15–30 hp) | – | – | 50 m (164 ft) | Yes1) | 50 m (£164) | Yes | – | – |
|  | – | – | 0.37-2.2 kW (0,5–3 hp) | 40 m (131 ft) | Yes1) | 40 m (£131) | Yes | 15 m (£49.2m) | – |
|  | 0.37-22 kW | – | – | – | – | – | – | – | – |
| A2 filter | (0,5–30 hp) |  |  |  |  |  |  |  |  |
| Emc | – | 0.37-4 kW | – | – | – | – | – | – | – |
| Life |  | (0,5–5,4 hp) |  |  |  |  |  |  |  |
| removed2) | – | – | 0.37-2.2 kW | – | – | – | – | – | – |
|  |  |  | (0,5–3 hp) |  |  |  |  |  |  |
|  | 0.37-7.5 kW | – | – | 5 m (16.4 ft) | Yes1) | – | – | – | – |
| A1 filter | (0,5–10 hp) |  |  |  |  |  |  |  |  |
| Emc | 11-22 kW | – | – | 5 m (16.4 ft) | Yes1) | – | – | – | – |
| Life | (15–30 hp) |  |  |  |  |  |  |  |  |
| removed2) | – | – | 0.37-2.2 kW | 5 m (16.4 ft) | Yes1) | – | – | – | – |
|  |  |  | (0,5–3 hp) |  |  |  |  |  |  |

EMC Emission (Filter type: internal)

- The frequency range between 150 kHz and 30 MHz is not compatible between IEC/EN 61800-3 and EN 55011 and is not  necessarily    included.

- Low ground leakage current. Compatible for working on ELCB/IT networks.

The test results in Table 2.14 were obtained using  a system with frequency converter (with mounting plate), external filter, engine and  protected  motor  cables.    The 3-phase 380–480 V frequency converter must be with built-in A1 filter.

38	Danfoss A/S © 05/2017  All rights  reserved. 	MG07B302